## Datix listing report
ID | Reported Date | Approval status | Category | Sub Category | Description | Action taken | Investigation Findings | Lessons learned
90561 | 2019-05-09 | Finally Approved | Fire Bedford Site Only | Fire Alarm - Cooking smoke / cooking heat | Fire Alarm activated @ 00:45 09/05/19 Location: Horseshoe Block Flat 3 Room 1 (ID 02/1/66) Activation due to burning candle in room | Craftsman on call attended, checked location to determine cause with Fire Service and reset system | Lit candle set off fire alarm. Tenant extremely apologetic. | Tenant has been spoken to - she is very sorry about this incident and has made a sincere apology. She understands that she should not use candles in The Horseshoe. No further action to be taken at this point.
91804 | 2019-06-26 | Finally Approved | Fire | Fire Alarm - Activated accidentally | Fire Alarm activation - Cygnet Wing - Orchard Ward Corridor MCP 92/2/16 date: 26/06/19; time:08:53 | Activation attended by Trust Fire Control Officer and Technician; source of activation identified (accidental activation of MCP) and system reset. | Break glass point accidentally actuated by BHT Porters. | Greater care to be taken when transporting items across the Trust.
92031 | 2019-07-04 | Finally Approved | Fire | Fire Alarm - Cooking smoke / cooking heat | Fire Alarm activation - Horseshoe - 2nd Floor Kitchen/Dining Area Detector: 27-D25 02/G/004 date: 03/07/19; time: approx. 11:00am | Activation attended by Trust Fire Control Officer and Maintenance Supervisor; source of activation identified (cooking in kitchen)and system reset. | Cooking (pot of rice) left unattended. Tenants contacted by Building Manager by email and educated on the dangers of leaving cooking unattended. Tenants also refreshed on their fire safety responsibilities whilst in residence at Horseshoe. | Tenants educated in the dangers of leaving cooking unattended.
92032 | 2019-07-04 | Finally Approved | Fire | Fire - False alarm | Fire Alarm activation - Link Corridor - Bed Store smoke/heat detector in 24/G/10 date: 04/07/19; time:13:53 | Activation attended by Trust Fire Control Officer and Technician; source of activation identified (excess temperature in store), detector disabled until room temperature reduces and system reset. | The opening of bed store door allows the hot air trapped in the store to be released - this sudden release hits the nearby detector head thus actuating the fire alarm. | In hot conditions the door to the bed store should be opened slowly in order to allow the trapped hot air to disperse before reaching the detector head. PS - The detector head has been relocated in the past due to previous actuations. It may require to be repositioned even further away from the bed store door opening area.
92498 | 2019-07-22 | Finally Approved | Equipment Problem - POD System | Missing / lost / not available | 64 patient samples from 20/07/1920 turned up in the laboratory early hours of 22/07/19. All had been stuck in the POD system | All samples were rejected due to age. See attached document for Winpath numbers of lost samples. | The issue was down to a line communication error, which once it was reset, it worked once and the lines were cleared of multiple PODs. It was also found that the PODs were being overloaded by staff on the wards, which will need to be addressed. | Any problems with the POD system should be reported in the first instance to avoid further issues. The maintenance team need to made aware of the issues immediately so that it can be resolved before it causes too much interruption to the trust. Out of hours the switchboard should be contacted, so that the on call engineer can send an engineer to fix the problem. The estates/maintenance have been recording the history of issues within the system and now have some planned maintenance and remedial works being carried out to address these issues on the POD system.
92579 | 2019-07-24 | Finally Approved | Environmental hazards | Heat | Theatre 9 - temperature reached 29 degrees Theatre 10 - temperature reached 27.1 degrees Both lists had to be stopped due to the risk of surgical site infection Theatre 9 - has had a temporary fix bringing the temperature down to adequate Theatre 10 - working to its maximum with no improvement possible, temperature continues to rise. | Theatre 10's list moved to theatre 2 in the afternoon. 3 of urology surgeon's patients were cancelled due to no theatre availability | Theatre 10 - Due to extremely high external temperatures which the air conditioning was not designed for and also the positioning of the cooling equipment above theatre 10 (in direct sunlight) the temperatures within the theatre rose to an unacceptable level. Once the external temperatures dropped temperatures within the theatre dropped also. Theatre 9 - the Trusts refrigeration service contractor was called to attend site and found problems with the refrigeration circuit compressors resulting in only 25% capacity of the chiller being available. Repairs were carried out enabling the temperatures within the theatre to be reduced. Further work is required and quotations are being obtained. | None. Extremely high external temperatures beyond those which the equipment is designed for puts a strain on the equipment.
92639 | 2019-07-26 | Finally Approved | Devices / Equipment - Medical | Failure of device / equipment | Power failure to x-ray system during coronary interventional procedure. Although power still supplied to lighting, haemodynamic system etc. UPS cabinet had alarm sounding from it. | Patient made safe. Procedure was near the end and stent had been safely deployed. Haemodynamic monitoring ok. Situation was explained to patient by Consultant Cardiologist. Estates manager attended immediately and found tripped switches. Issue now resolved. At time of failure a radiation safety light bulb was being replaced. This has taken place numerous times previously, with no problems. On this occasion, Estates believe the neutral and earth may have been shorted causing the earth leakage to trip in PDB and C30K. Estates tested this theory and both breakers tripped. In future, all radiation warning light bulbs will be replaced only when the x-ray system is not in use. Team will be made aware. | The cause was exactly as described in the incident details: "At time of failure a radiation safety light bulb was being replaced. This has taken place numerous times previously, with no problems. On this occasion, Estates believe the neutral and earth may have been shorted causing the earth leakage to trip in PDB and C30K. Estates tested this theory and both breakers tripped" | As described in the incident report in future, all radiation warning light bulbs will be replaced only when the x-ray system is not in use. Team will be made aware.
92724 | 2019-07-31 | Finally Approved | Fire | Fire Alarm - Faulty detector | Fire Alarm activation - Pathology - Shared Workstations smoke/heat detector in 48/1/30 date: 23/07/19; time:11:51 | Activation attended by Trust Fire Control Officer and Technician; source of activation identified (faulty head), detector temporarily isolated from system and system reset. | Faulty detector head - head replaced and alarm system reset | On-going maintenance of fire alarm system
93596 | 2019-09-04 | Finally Approved | Accidental Injury or Personal Accident (incl. Falls) | Exposure to/Contact with Harmful/Hazardous Substance | Fumes coming through the ventilation system coming from car parking reconfiguration behind cygnet wing. Staff Nurse from Riverbank asthmatic and this triggered an asthma attack. | Taken to Emergency Department for management of asthma attack, reviewed by critical care outreach team and admitted to AAU | Road linings were being removed on the perimeter road near Cygnet Wing using a burning torch. The work was taking place approx. 10m away from a first floor ventilation air intake louvre. The fumes entered the ventilation system and were drawn into the ward. | Consideration should be given to the location of ventilation air inlet ducts when using a burning torch to remove road markings. If it is not appropriate to use a torch then the road linings are to be painted over.
93603 | 2019-09-04 | Finally Approved | Accidental Injury or Personal Accident (incl. Falls) | Exposure to/Contact with Harmful/Hazardous Substance | Fumes coming through ventilation system on Riverbank coming from car park development work. Nurse with asthma started coughing and was short of breath | Immediately removed from area where fumes were coming through. Inhaler taken. Improved enough to return to work, however after 3 hours unable to continue with shift | This incident was also reported on IR 70518 "Road linings were being removed on the perimeter road near Cygnet Wing using a burning torch. The work was taking place approx. 10m away from a first floor ventilation air intake louvre. The fumes entered the ventilation system and were drawn into the ward" | As reported on IR 70518 "Consideration should be given to the location of ventilation air inlet ducts when using a burning torch to remove road markings. If it is not appropriate to use a torch then the road linings are to be painted over"
93656 | 2019-09-06 | Finally Approved | Environmental hazards | Ventilation (heating, air conditioning) | Ventilation system in theatre 7 stopped working on 3 separate occasions, approx. 9.30am on Thursday 5/9/19, 9.30am on Friday 6/9/19 and 11am on Friday 6/9/19. | Immediate contact made with bleep6002. Senior theatre nurse informed. | Maintenance attended on Thursday and Friday and on each occasion, as the theatre was in use, simply reset the supply fan motor to bring the fan back on line. Further investigation took place on Saturday morning 10th Sept when the theatre was not in use and the fan could be safely switched off. The supply fan inverter parameters were checked and adjusted as required. | None
94244 | 2019-10-01 | Finally Approved | Environmental hazards | Water / damp | Lower theatre 7 flooding today; anaesthetic room, doctor's room, corridor towards reception area, and outside theatre 7 main door. | Domestics informed, maintenance informed. Moorfields management informed. Datix done. | Upon investigation the leak has subsided and was not present. Reactionary remedial works on numerous areas on the roof had been completed following the leak. | Emergency leaks must be reported immediately to Maintenance to take appropriate action.
94414 | 2019-10-08 | Finally Approved | Infection Control | Decontamination issue | Red specks found in Decontamination Endoscopy washroom area. they looked like tiny bits of plastic.it appeared also in AER machines filters. | identified that these specs come from tray liner put on scope tray after use. keep processing scopes as per infection control advise as we already flush and wipe scopes after use. if any spec identify in washer scopes to be reprocessed. reported to the supplier of these tray liners as they seems to be low quality. taken all faulty (low quality) batch of tray liner out of use. | When tray liners checked - of inferior quality, batch No tray liners removed and quarantined. New batch No of tray liners put into use - better quality. Supplier informed - awaiting feedback. Red flecks found in manual cleaning sinks, staffs gloves and other areas of department diminished within 2 hours of implementation of new tray liners. Staff continued to flush and wipe scopes from washers and no scopes were contaminated with red flecks and returned to wash for re-processing. Users Endoscopy and Infection control informed of issue and confirmed that reprocessing of scopes could continue | Quality of products - if there are changes to the quality of a product from previous lot no this needs to be brought to the attention of managers immediately.
94639 | 2019-10-17 | Finally Approved | Environmental hazards | Cold | Pharmacy heating is not working. | Called the states department twice - no action yet. | Following an inspection it was found that steam control valves were sticking resulting in poor temperature control. The valves were replaced/serviced as required and then tested - system now running ok | Planned Preventative Maintenance may need tighter control to ensure that all aspects of the control system are adequately checked.
97542 | 2020-02-19 | Finally Approved | Patient documentation | Temporarily unavailable / delay in accessing | Medical Records Library (Warehouse Block B) roof continually leaking when it rains causing slip hazard as well as damage to patient Medical Records. Most recently over the weekend of February 15th & 16th with storms and heavy rain the roof leaked again in several places causing considerable damage to a minimum of five (5) sets of patients records. This roof problem has been an on-going issue for many years and reported to Estates Management via MICAD, the most recent Call No being 183124. | Reported several times via MICAD to Estates Management | DATIX was received on 30/04/2020. At the time of investigation the leaks had already been addressed by the Maintenance Department so no leaks were present. | All maintenance issue should be reported via the intranet MICAD job reporting system immediately. Any emergency works should also be relayed verbally.